## Slide 1
UL217认证测试项目介绍
KAI WANG
X-Sense Innovations Co., Ltd.

## Slide 2
Fire Safety Laws & Legislation

## Slide 3
UL 217
Release Date
Sixth Edition – August, 2006
Seventh Edition – June, 2015(未正式生效)
Eighth Edition – October, 2015
Ninth Edition – January, 2020
Information from ETL via e-mail
The Effective Date for either the 8th edition or the 9th edition is June 30, 2024. We do not have a separate date for the 9th edition only.
The 10th edition has not been released yet but I expect it to be approved sometime within the next year.

## Slide 4
认证机构
UL
ETL

## Slide 5
新版标准竞品获证情况

## Slide 6
测试项目介绍

## Slide 7
测试环境
The smoke alarm shall be installed in an environment so as to permit accurate monitoring of the conditions in (a) – (e). Unless otherwise specified, the following conditions shall be established and maintained throughout the test: a) Ambient temperature at 23 ±3°C (73.4 ±5°F) or a higher temperature if specified by the manufacturer, b) Relative humidity at 50 ±20 percent, c) Oxygen concentration at 20.9 ±1 percent, d) Barometric pressure of 101 ±4 kPa of mercury (760 ±30 mm), and e) Supply voltage, if applicable, adjusted to 100 percent of rated input voltage.

## Slide 8
测试结果判断
During or immediately after performance tests, the sensitivity of the detectors shall not vary more than ±1 percent per foot obscuration from the value recorded prior to the test.
And the alarm shall emit neither a fault signal nor an alarm signal during the test.

## Slide 9
Normal Operation Test
产品的正常功能检查，包含报警优先级、故障指示、静音功能、语音模式、报警发音模式以及其他各项功能检查确认。

## Slide 10
Battery trouble voltage determination
确认烟雾警报器低电压值。

## Slide 11
Sensitivity Test

## Slide 12
Velocity-Sensitivity Test
Air velocity 32 fpm(0.16 m/s)
Air velocity 150 fpm( 0.76 m/s)
Directionality Test
确认最高最低灵敏度方向

## Slide 13
Smoke Entry (Stack Effect) Test
Air Flow 300英尺/分钟风速

## Slide 14
Lamp Interchangeability Test (Photoelectric)
The sensitivity of an alarm employing a replaceable light source shall vary not more than 1obs.
And shall comply with the requirements of the Sensitivity Test, when tested with the intended replacement lamps.

## Slide 15
Stability Tests

## Slide 16
Fire Tests

## Slide 17
Fire Tests
纸火--4分钟内报警

## Slide 18
Fire Tests
木材--4分钟内报警

## Slide 19
Fire Tests
可燃液体--4分钟内报警

## Slide 20
Fire Tests
聚氨酯泡沫-- --<5obs内报警（第8版）

## Slide 21
Smoldering Smoke Test
木材-- --<12obs内报警

## Slide 22
Smoldering Smoke Test (第8版)
聚氨酯泡沫-- --<12obs内报警

## Slide 23
Cooking Nuisance Smoke Test (第8版)
煎牛排油烟-- --1.5obs前不可报警

## Slide 24
Go/No Go Flaming Polyurethane Foam Test (第9版)
煎牛排油烟-- --1.5obs前不可报警（到达1.5obs烟雾浓度后需10秒内停止煎牛排）
聚氨酯泡沫-- --<5obs内报警

## Slide 25
Temperature Test
在任何操作条件下，报警器中使用的材料或部件的温升不得超过表47.1中所示的温升

## Slide 26
Overload Test
AC机型.
1.15倍额定电压供电
6次报警/分钟，50个循环
Endurance Test
5秒报警，1分钟10次，共6000个循环

## Slide 27
Variable Ambient Temperature Test
Operation in high and low ambient
0度低温灵敏度
49度高温灵敏度
Effect of shipping and storage
a temperature of 70°C for a period of 24 hours, let to cool to room temperature for at least 1 hour
a temperature of -30°C for at least 3 hours, and then permitted to warm up to room temperature for at least 3 hours

## Slide 28
Leakage Current Test
The leakage current of an alarm not operating from a primary battery shall not exceed 0.5 milliampere
浪涌雷击/抗干扰等方面的测试
Transient Tests

## Slide 29
Abnormal Operation Test
烟雾报警器应在异常(故障)条件下连续工作，不产生火灾危险。
烟雾报警器应在使用过程中在电路异常故障情况下运行，同时连接到表所规定的电源上。不得有火焰、熔化的金属或者其他火灾的表现。

## Slide 30
Overvoltage and Undervoltage Tests
1.1 VR
0.85 VR
BAT VLB
Static Discharge Test
10,000 volts DC for at least 2 seconds

## Slide 31
Dust Test
测试时间 15分钟
测试过程中报警、故障提示 or 测试前后灵敏度差异不超过1obs.

## Slide 32
Humidity Test
168小时
湿度 93+/-2RH%
温度 40摄氏度
Vibration Test / Jarring Test
验证产品结构的可靠性

## Slide 33
Corrosion Test
temperature of 23 ±2°C , maintained at 93+/2 percent relative humidity
硫化氢1000±50 PPM 10天
二氧化碳10 000±500 PPM &二氧化硫5000±250 PPM 10天
Alternate Corrosion Test (21-Day): temperature of 30 ±2°C (86 ±3°F) and the relative humidity at 70 ±2 percent，100±10 (ppb) (H2S) ；20 ±5 ppb (Cl2)；200 ±50 ppb (NO2) (第8版)

## Slide 34
Battery Tests
a) Room Ambient – 23 ±3°C (73.4 ±5°F), 30 – 50 percent relative humidity, 760 mm Hg. b) High Temperature – 45°C (113°F). c) Low Temperature – 0°C (32°F). d) Humidity – 30 ±2°C (86 ±3°F), 85 ±5 percent relative humidity.
可更换-测试时间1年
不可更换-测试时间10年
低电状态后，a minimum of 4 minutes of alarm, followed by 7 days of trouble signal

## Slide 35
Audibility Test
temperature of 121°C (250°F) for a period of 4 minutes
DB>85
灵敏度变化<1obs
Survivability Test
DB>85, 3.05m

## Slide 36
Tests of Thermoplastic Materials
高温老化—7天90度，或28天70度，相对湿度0~10%RH
Flame test—确认壳料阻燃等级是否满足要求

## Slide 37
Battery Replacement Test
50 cycles of battery removal and replacement, at a rate not to exceed 6 cycles per minute, without any reduction in contact or mounting integrity.
验证电池接触装置可靠性
Polarity Reversal Test
证实烟雾警报器即使在电池极性连接错误后，仍能恢复正常工作。

## Slide 38
Electric Shock Current Test
验证产品维护时的电气安全性是否满足要求
Power Supply Tests
当产品使用独立电源时，验证此电源的是否满足要求

## Slide 39
Fire Test (Heat Detector)
A heat detector, provided as part of a single station smoke alarm assembly, shall comply with the Standard for Heat Detectors for UL 521
Accelerated Aging Test
14 days，66 °C , 0 – 10 percent relative humidity
10 cycles of change of air velocity from 0 to 1.5 m/s.

## Slide 40
Drop Test
警报器应能承受从7英尺（2.1米）高度跌落到混凝土地板上，五次
该测试不适用于固定安装的报警器（ This test is to be conducted only on smoke alarms intended for transient use, such as a travel alarm, and is not to be conducted on alarms intended for stationary installation.）
Conformal Coatings on Printed-Wiring Boards
验证保护涂层是否满足要求，高温/高湿/老化/加高电压，涂层材料不得因处理而剥落或其他劣化现象，以及不得有电介质击穿的迹象。

## Slide 41
附加项--适用于房车、船的烟雾警报器补充测试项
Variable Ambient Temperature and Humidity Test
Corrosion (Salt Spray) Test
Vibration Test
……

## Slide 42: THANKS